# Temperature Measurement Instrumentation Standards

## Introduction

Temperature measurement is fundamental to controlling reaction rates, product quality and equipment integrity in a refinery. These standards draw on API 551, ISA 20, ISA 5.1 and ASME PTC 19.3 requirements to ensure reliable and accurate temperature measurement devices.

## Applicable Standards

These standards provide requirements for the design, installation and documentation of temperature‑measurement instruments:

- API 551 – Process Measurement Instrumentation – temperature‑measurement guidelines.

- ISA 5.1 – Instrumentation Symbols and Identification – standard P&ID symbols.

- ISA 20 – Data Sheets – information to capture for temperature instruments.

- ASME PTC 19.3 TW – Thermowell Design – rules for thermowell stress and vibration.

- ASTM E1137/E1137M – Industrial Platinum RTDs – specification for platinum RTDs.

- IEC 60584‑1/IEC 60584‑3 – Thermocouples – reference tables and tolerances for base‑metal and noble‑metal thermocouples, including limits of error【658884660910242†L65-L168】.

- IEC 60751 – Industrial Platinum Resistance Thermometers (Pt 100) – requirements and tolerances for platinum resistance temperature detectors (RTDs) used in industrial process control【658884660910242†L65-L168】.

## Equipment Types

- Resistance Temperature Detectors (RTDs): spring‑loaded platinum RTDs with 316 SS thermowells; 4–20 mA transmitters with ±0.1 % of span accuracy【51948133245220†L3910-L3925】.

- Thermocouples: type K, J or T; mineral insulated with stainless steel sheaths; transmitter accuracy ±0.25 % of span.

- Bimetallic dial thermometers: 5‑inch dial indicators with stainless steel stems; ±1 % of full range accuracy【51948133245220†L3936-L3943】.

- Temperature switches: capillary or bimetallic switches with SPDT contacts and adjustable setpoints【51948133245220†L3985-L3999】.

- Thermowells: bored from solid barstock, 316 SS; connections ¾‑ or 1‑inch NPT; minimum wall thickness 3/16 in【51948133245220†L3949-L3975】.

## Selection and Design Criteria

- Sensor type – use RTDs for higher accuracy and stability; thermocouples for high temperature or fast response applications.

- Range and accuracy – specify spans that encompass the normal operating range; RTD transmitter accuracy ±0.1 % of span【51948133245220†L3910-L3925】; bimetallic dial gauges ±1 %【51948133245220†L3936-L3943】.

- Thermowell design – design wells per ASME PTC 19.3; choose insertion length to minimise vibration; ensure U‑length within manufacturer’s allowable limits【51948133245220†L3959-L4017】.

- Material compatibility – select sheath and well materials compatible with process fluid; typically 316 SS or exotic alloys for corrosive media.

- Output signal – temperature transmitters shall provide 4–20 mA DC output; include integral LCD indicator where local indication is required.

## Installation Guidelines

- Location: mount sensors in well‑mixed zones; avoid dead legs or stagnant pockets.

- Thermowells: install with isolation valves for removal; orient vertically where possible; use thermal grease for better conduction.

- Wiring: use shielded thermocouple/RTD wire; limit cable runs to prevent signal loss; maintain proper polarity for thermocouples.

- Bimetal thermometers: install at eye level; ensure dial visibility; use thermowells to permit replacement without breaking process seal.

### Thermocouple Installation Best Practices

Good installation practices ensure that thermocouples provide accurate and reliable measurements. Follow these recommendations【352185073463712†L775-L835】:

- Protect thermocouples from the environment – Use sheathed or double‑protected thermocouples or install bare wire sensors inside clean, sulfur‑free protection tubes to avoid oxidation, corrosion and contamination【352185073463712†L775-L835】.

- Select proper wire gauge – Heavier gauge thermocouple wire offers greater thermal stability and mechanical strength; select gauge based on process temperature and mechanical stresses【352185073463712†L775-L835】.

- Placement – Avoid placing thermocouples directly in flame impingement or in areas with high air velocity that cause cooling errors; instead install them in well‑mixed zones【352185073463712†L775-L835】.

- Immersion depth – Immerse the sensing tip at least ten times the thermowell outside diameter into the process fluid to ensure accurate temperature measurement; maintain consistent immersion depth after removal and re‑installation【352185073463712†L775-L835】.

- Maintenance program – Implement preventive maintenance with regular inspection of thermocouple junctions, extension wires and protection tubes; replace damaged components and recalibrate as necessary【352185073463712†L775-L835】.

## Calibration and Testing

- Calibrate transmitters and indicators at multiple points across the range; verify RTD and transmitter as an assembly.

- Thermocouples should be checked for continuity and insulation resistance; calibrate in a dry‑block calibrator.

- Temperature switches shall have setpoints bench‑tested; verify deadband.

## Safety Considerations

- Select intrinsically safe transmitters or explosion‑proof heads for hazardous areas.

- Thermal expansion can cause stresses; design thermowells to withstand process flow‑induced vibration.

- For high temperature (>400 °C) service, consider thermocouple types and materials rated for temperature.

## Data Sheet Requirements

Document tag number, service, sensor type, range, output, accuracy, process connection, thermowell material and insertion length, ambient conditions and hazardous area classification.

## Maintenance and Inspection

- Inspect thermowells and sensors periodically for corrosion, erosion or cracking; replace if thinning observed.

- Verify transmitter calibration and replace failed indicators.

- Replace bimetallic gauges showing pointer drag or damage.